## Draft 1
Volume | Stakeholder Organization | Measure # | Measure | Page | Comment scope | Comment text | Author | VEIC Response | Changes made | 21-Jul TAC | 26-Jul TAC2 | 2-Aug TAC3 | In Memo
2 | Ameren | 4.1.11 | 4.1.11 Commercial LED Grow Lights | 38 | PPF Equivalence Method | Prior methods were easy to implement in a prescriptive lighting program. The implementation team has concerns that the new methodology makes this harder to implement. Can an example be added, as the use of this new equation is unclear and the units do not appear to work | Vaughn, Andrew C | Example calculations and units were added to the characterization. Additional clarification on new analysis approach was provided by workpaper authors in TAC on 7/26. Units were confirmed to work out accurately in algorithm. | Edits made |  |  |  | Y
2 | Ameren | 4.4.9 | 4.4.9 Air and Water Source Heat Pump Systems | 299 | In order to allow for existing inventory meeting the previous federal standards and IECC 2021 guidelines, this measure characterization will adopt these federal appliance standards and IECC 2021 guidelines as the baseline on January 1, 2024. | Recommend changing to "In order to allow for existing inventory meeting the previous federal standards and IECC 2021 guidelines, this measure characterization will adopt these federal appliance standards and IECC 2021 guidelines as the baseline on January 1, 2024." | Vaughn, Andrew C | Discussion on-going. Ultimately, VEIC disagree with the revision. The recommendation was to include having the TRM adopt IECC 2021 guidelines along the same timeframe as the new heat pump standards. For new construction projects permitted after the state adoption date, they will be required to adhere to IECC 2021 and it becomes the effective baseline for this measure. The prescriptive characterization is able to delay adopting the new federal standards by a year because it assesses, in lieu of program intervention, what would the customer have installed. In that case, its the minimum efficiency requirements of available equipment. This isn't the case for new construction applications as they are required to follow state code, which has a near 100% compliance record in Illinois. Municipality grace periods may provide additional buffer and clarity to this point once they became known as code adoption by Illinois is still TBD. | No changes made, discussion on-going pending code adoption dates | Jake. Discussed on 7/21 TAC call. Discussed on 7/25 Energy Codes Working Group Call | Jake |  | N/A
2 | Ameren | 4.4.13 | 4.4.13 Package Terminal Air Conditioner and Package Terminal Heat Pump | 328 | PTAC or PTHP | Replace "PTAC or PTHP" with "HVAC system" to account for fuel-switching | Vaughn, Andrew C | Agreed. | Edits made | Not needed |  |  | Y
2 | Ameren | 4.4.13 | 4.4.13 Package Terminal Air Conditioner and Package Terminal Heat Pump | 328 | PTAC or PTHP for the | Replace with "…existing HVAC equipment for the…" to account for fuel-switching | Vaughn, Andrew C | Agreed. | Edits made | Not needed |  |  | Y
2 | Ameren | 4.4.15 | 4.4.15 Single-Package and Split System Unitary Air Conditioners | 356 | In order to allow for existing inventory meeting the previous federal standards and IECC 2021 guidelines, this measure characterization will adopt these federal appliance standards and IECC 2021 guidelines as the baseline on January 1, 2024. | Recommend changing to "In order to allow for existing inventory meeting the previous federal standards and IECC 2021 guidelines, this measure characterization will adopt these federal appliance standards and IECC 2021 guidelines as the baseline on January 1, 2024. | Vaughn, Andrew C | See similar comment to 4.4.9 Air to Water Source Heat Pump Systems | No changes made, discussion on-going pending code adoption dates | Jake. See above |  |  | N/A
2 | Ameren | 4.4.37 | 4.4.37 Unitary HVAC Condensing Furnace | 470 | Note: new Federal Standards applicable to all gas furnaces become effective January 1, 2023. | Other measures delay adoption of new CFR until 1/1/2024 to allow non-compliant inventory to clear through the supply chain. It seems this measure should follow suit for consistency. | Vaughn, Andrew C | Agreed. Will ammend adoption of this standard to take effect in the TRM on 1/1/2024. | Edits made | Not needed |  |  | Y
2 | Ameren | 4.4.48 | 4.4.48 Small Commercial Thermostats | 549 | For midstream programs, assume a value of 8.2 | Disagree with 8.2. Many ducted and rooftop commercial systems have resistance heat. CBECS assumption appears more appropriate | Vaughn, Andrew C | VEIC believe that the types of thermostat that this measure represents are not used for systems with resistance heat and that assuming a heat pump for this assumption is appropriate. | None | Sam |  |  | N/A
2 | Ameren | 4.4.59 | 4.4.59 Ductless Heat Pumps | 637 | Ductless | Several variables recently introduced regarding HSPF & HeatLoadFactor added to this measure which need further review. | Vaughn, Andrew C | 7/12 Working Group and 7/26 TAC focused on these measures. Draft 2 contains current standing on these issues. We will continue the conversations and try and reach consensus on all open issues. | None |  | Sam |  | N/A
2 | Ameren | 4.8.27 | 4.8.27 C&I Air Sealing | 960 | Sealing | Ok with switching to just 4.8.27 | Vaughn, Andrew C | Discussed with TAC. Appears proposal to replace 4.8.16 Commercial Weather Stripping with new measure 4.8.27 C&I Air Sealing is preferred approach. | 4.8.16 Commercial Weather Stripping measure retired. | Sam |  |  | Y
2 | Ameren | 4.8.28 | 4.8.28 High Speed Overhead Doors | 971 | Entryway Orientation | Please add Unknown (average) orientation to all tables in this section (similar to 4.8.29) | Vaughn, Andrew C | Agreed. Added. | Unknown values added to two tables. | Not needed |  |  | Y
2 | Nicor Gas | 4.4.3 | 4.4.3 Process Boiler Tune-Up | 274 | 1 years | The other TRM research provided varies between 12 months to 2 years. The Michigan Energy Measures Database (MEMD) is the only source with process tune-ups and has a measure life of 2 years. Therefore, should this be 2 years? | Nicor Gas | Per industry standards, depending on use, boilers should be tuned at least annually; high use boilers at least twice annually. (https://www1.eere.energy.gov/femp/pdfs/om_9.pdf). To further support the previous statement, the Illinois Compiled Statutes Safety Act indicates that 1) power boilers should be inspected annually internally and externally. However, other TRMs do vary between 12 months and 2 years. Iowa leverages 12 months whereas Focus on Energy, MEMD, and Minnesota all use 2 years. Franklin Energy provided the updated workpaper. For reference discussed in TAC on 06/07 | Edits made. Revised from 1 year to 2 | Jake. Discussed on 7/21 TAC call. Recommendation to ammend measure life to 2 years |  |  | Y
2 | Nicor Gas | 4.4.3 | 4.4.3 Process Boiler Tune-Up | 274 | is $0.83/MBtu/h | We are working on provided program data analysis to update the deemed measure cost. | Nicor Gas | Update pending, no response necessary |  | Not needed |  |  | N/A
2 | Opinion Dynamics | 4.2.1 | 4.2.1 Combination Oven | 77 | 3.412/ 1,000,000] | From Tyler Sellner: Should this be 3,412/1,000,000? Perhaps not, given how some of the parameters are defined. | Alex Caratti | No, the variables in this measure are expressed as Wh (not kWh) so the appropriate conversion is 3.412 BTU/Wh | None | Sam |  |  | N/A
2 | Opinion Dynamics | 4.2.7 | 4.2.7 ENERGY STAR Fryer | 126 | * 3.412/1,000,000 * | From Tyler Sellner: Should this be 3412/1,000,000? Perhaps not, given how some of the parameters are defined. | Alex Caratti | No, the variables in this measure are expressed as Wh (not kWh) so the appropriate conversion is 3.412 BTU/Wh | None | Not needed |  |  | N/A
2 | Opinion Dynamics | 4.2.7 | 4.2.7 ENERGY STAR Fryer | 134 | / 1,000 | From Tyler Sellner: Is this appropriate? I don't see this factor in 4.2.1, 4.2.3, or 4.2.5. | Alex Caratti | Wherever the measure variables are Wh this is appropriate to convert to kWh. Note that in measure 4.2.1 the ∆kWh algorithm in cost effectiveness section should divide by 1000. | /1000 added to ∆kWh algorithm in cost effectiveness section of measure 4.2.1. | Sam |  |  | Y
2 | Opinion Dynamics | 4.2.8 | 4.2.8 ENERGY STAR Griddle | 136 | 3.412/1,000,000 | From Tyler Sellner: Should this be 3412/1,000,000? | Alex Caratti | No, the variables in this measure are expressed as Wh (not kWh) so the appropriate conversion is 3.412 BTU/Wh | None | Not needed |  |  | N/A
2 | Opinion Dynamics | 4.2.8 | 4.2.8 ENERGY STAR Griddle | 143 | / 1,000] | From Tyler Sellner: Is this appropriate? I don't see this factor in 4.2.1, 4.2.3, or 4.2.5. | Alex Caratti | This is correct - since the variables are in Wh. | None | Sam |  |  | N/A
2 | Opinion Dynamics | 4.3.2 | 4.3.2 Low Flow Faucet Aerators | 212 | Unknown | From Brooke Bakish: Inconsistency, %Electric_DHW and %Fossil_DHW for unknown do not add to 100% here. See note above. | Alex Caratti | Thank you. Upon discussion with TAC, a 2015 AIC Potential Study is proposed as a better reference than current assumptions (based on residential installations) and so this has been replaced with 27.6% electric and 72.4% fossil DHW. | Updates to %Electric and %Fossil hot water in 4.3.2 Low Flow Faucet Aerator, 4.3.3 Low Flow Showerheads and 4.3.8 Controls for Central Domestic Hot Water. | Sam |  |  | Y
2 | Opinion Dynamics | 4.3.8 | 4.3.8 Controls for Central Domestic Hot Water | 242 | assume 84%. | Citation needed | Alex Caratti | As above, source has been updated. | Souce updated. | Not needed |  |  | Y
2 | Opinion Dynamics | 4.8.23 | 4.8.23 Lithium Ion Forklift Batteries | 943 | diesel | This measure repeatedly references diesel fuel. Diesel is not referenced in the policy manual fuel conversion tables and this may be confusing to parties in the future for things like cost-effectiveness testing. It might be worthwhile to note that from an energy perspective (e.g. energy content) that diesel can be considered to be the same thing as fuel oil (which is defined and discussed elsewhere), but from a cost perspective (e.g. avoided cost of consumption in a fuel switch situation) diesel costs are distinct from fuel oil costs. | Zachary Ross | After discussion in TAC we have added Diesel to the conversion table in volume 1. | Added diesel to Volume 1 table. | Sam |  |  | Y
2 | Opinion Dynamics | 4.8.23 | 4.8.23 Lithium Ion Forklift Batteries | 945 | [1] | These efficiency values, per the footnote, assume an energy content of 91,542 BTU/gallon of propane. That is inconsistent with the Policy Manual defined conversion of 91,333 BTU/gallon of propane. The footnote does not explain what the energy content assumed for diesel (fuel oil) is, but similarly it needs to be aligned with the Policy Manual defined conversion of 138,500 BTU/gallon. | Zachary Ross | VEIC sent these comments to CLEAResult who recalculated based on the policy manual values. | EEbase and resultant savings estimates update. | Sam |  |  | Y
2 | Opinion Dynamics | 4.8.23 | 4.8.23 Lithium Ion Forklift Batteries | 947 | EFBASE | This term should be "EEbase" not "EFbase" | Zachary Ross | Thank you. Fixed | Typo fixed | Not needed |  |  | Y
2 | Opinion Dynamics | 4.8.24 | 4.8.24 Building Operator Certification | 950 | .274342 kWh | From Tyler Sellner: Using the values in the table, you get 0.267 | Alex Caratti | These are older comments and were discussed in a TAC call on June 21. The difference is due to significant digits and rounding. Mike Frischmann at EcoMetric provided an update to this as well as provided a description as to why there may be slight differences in this due to not showing the full evaluation results so the user can derive the deemed savings factor themselves compared to the one given. | Done | Not needed |  |  | N/A
2 | Opinion Dynamics | 4.8.24 | 4.8.24 Building Operator Certification | 951 | 46316 | From Tyler Sellner: Using the values in the table you get 0.0047 | Alex Caratti | See above | Done | Not needed |  |  | N/A
2 | Verdant Associates | 4.5.4 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp |  | 92.9% | We agree with discounting future installations. However, we'd like further guidance on claiming carryover savings for CY2021 Year 3 installations to be included in the TRM. Should 3rd year CY2021 carryover be discounted and claimed in CY2022 or should savings be claimed in CY2023? Claiming these savings in 2023 would be complaint with v10 of the TRM, but it would results in inconsistent "accounting" methods applied in CY2022. We feel that claiming and discounting 3rd year savings in CY2022 would be the most appropriate way to align accounting for future installations. We recommend adding a note clarifying a appropriate apprach | Ethan Barquest | This is dealt with in the v10 errata. Basically for 2021 and 2022 purchases with carry over in 2023 and 2024, the errata provides the appropriate set of assumptions (namely use the v10 assumptions with the prescribed year of mid life adjustment). If this does not answer this concern, please let us know. | None |  |  |  | N/A
3 | Ameren | 5.1.2 | 5.1.2 ENERGY STAR Clothes Washers | 12 | %Electric_Dryer | %Electric Dryer is listed at 38% based on 2009 RECS data. The 2013 AIC Potential study has %Electric Dryer at 63% SF and 51% MF. The 2015 AIC Potential Study has: 68.8% SF and 69.8% MF. | Froio, Zach | Thank you. We agree this is likely a much better source for this assumption so propose using the 2015 study values to update. | %Electric / %Fossil Dryer assumptions updated and resulting savings updated with this and new %Electric/%Fossil DHW assumptions | Sam |  |  | Y
3 | Ameren | 5.1.2 | 5.1.2 ENERGY STAR Clothes Washers | 13 | ΔWater (gallons) | DeltaWater (gallons) is not defined until page 15. Recommend either adding a reference to the later section or define it on p.13. | Froio, Zach | Agreed. Added. | Definition added. | Not needed |  |  | Y
3 | Ameren | 5.1.7 | 5.1.7 ENERGY STAR and CEE Tier 2 Room Air Conditioner | 37 | 246 | Something seems to be wrong with AIC's weighted average FLHs. If the state average in v.10 had been 248 and is now 245 and ComEd's new value is 226, AICs value needs to be higher than 246. | Froio, Zach | Upon review with the TAC, determined a better approach would be to use actual accounts as the weighting for Ameren and only weight zones 1 and 2 for ComEd. | All tables showing Ameren and ComEd weighted values have been updated | Sam |  |  | Y
3 | Ameren | 5.1.9 | 5.1.9 Room Air Conditioner Recycling | 46 | 246 | Something seems to be wrong with AIC's weighted average FLHs. If the state average in v.10 had been 248 and is now 245 and ComEd's new value is 226, AICs value needs to be higher than 246. | Froio, Zach | As above | As above | Sam |  |  | Y
3 | Ameren | 5.1.10 | 5.1.10 ENERGY STAR Clothes Dryer | 50 | Vented Electric Heat Pump, Compact (< 4.4 ft3) | The values for Heat Pump and hybrid HP units don't agree well with the ES list available on 7/9/22. Our analysis finds the following average CEF_eff values: ES Compact: 3.36; ES, Standard: N/A; ES Most Efficient, Compact: 6.21; ES Most Efficient, Standard: 6.53. Additionally, the category titles should combine "Vented or Ventless". Of the 38 HP dryers on the ES QPL, only 3 are vented. | Froio, Zach | VEIC also looked at the QPL and agree with these values. Also agree with removing vented/ventless for heat pump units. | Updated CEFeff based on updated QPL. Removed "Vented" from heat pump name. | Sam |  |  | Y
3 | Ameren | 5.1.13 | 5.1.13 Income Qualified: ENERGY STAR and CEE Tier 2 Room Air | 63 | 364 | The SF and MF values look believable (as a weighted average compared to the satewide average), but the Weatherized MF for AIC looks wrong -- ComEd: 338, AIC: 364, Statewide:362. The AIC value would need to be notably higher than the statewide average value. | Froio, Zach | Upon review with the TAC, determined a better approach would be to use actual accounts as the weighting for Ameren and only weight zones 1 and 2 for ComEd. | All tables showing Ameren and ComEd weighted values have been updated | Sam |  |  | Y
3 | Ameren | 5.1.14 | 5.1.14 Residential Induction Cooktop | 65 | 1200 | In "Deemed Measure Cost", incremental cost of $1,200 seems high. "Frigidaire Gallery CGIH3047V or GCRI3058AF" is $1,099 and the non-induction version is $899 (GCRE3038AF) (difference of $200). "Samsung NE63B8211SS" is $1298 and "Samsung NE63T8111SS" is $878 for a difference of $420. | Vaughn, Andrew C | Upon review, VEIC costs were based on the Emerging Technology Award units specifically and are not a good reflection of the average incremental cost for all induction units. Reverted to the source of the cost assumption provided in the workpaper (although final values different to workpaper). | Cost assumption updated. | Sam |  |  | Y
3 | Ameren | 5.1.14 | 5.1.14 Residential Induction Cooktop | 66 | IAECee | Recommend making the variable names consistent. For example, the entry goes back and forth between IAEC_ee and AEC_ee (see kWh savings example). A full reference is needed for the Frontier Energy Residential Cooktop Performance and Energy Comparison Study and the paper should be archived with the TRM technical material. | Froio, Zach | Agree to fix the efficient term in the example calculation to IAEC. Reference placed in folder | Fixed IAEC term throughout. Reference document added to folder. | Sam |  |  | Y
3 | Ameren | 5.1.15 | 5.1.15 Residential Bolt-On Smart Dryer Sensor | 70 | This measure relates to the installation of a bolt-on smart wifi enabled dryer sensor with cloud data storage access on a residential gas-fired dryer | The measure description refers to the device added to "a residential gas-fired dryer.", but the measure savings are clearly developed for electric or gas dryers.There are other areas of the variable definitions where "gas dryer burner element" is refered to for Electric savings. The example at the end of the entry uses N_cycles = 400 rather than the 283 cycles per year in the electric energy savings section. | Froio, Zach | As of June 17, 2022 the only model on the market (SmartDry) was discontinued, and since there are currently no comparable product on the market, and the savings values are based on a field study with the now defunct SmartDry, this measure has been put on hold. If a new product were to enter the market, this measure would need to be reviewed prior to adding it back into the TRM volume. Therefore this measure will be removed for v11. Note after draft 2 VEIC were informed that an alternative manufacturer had been found to produce the product - therefore measure was reinstated. In response to this comment: Updated language to reflect addition of electric dryer option to measure. The actual number of cycles should be used, if known. In the example this value was known to be 400 cycles per year | Measure removed. Reinstated after draft 2 and electric baseline edits added. | Deirdre |  |  | Y
3 | Ameren | 5.3.1 | 5.3.1 Air Source Heat Pump | 81 | Air Source Heat Pump | General concerns over changes being proposed that were not included in Draft 1 to ensure that all technical details are fully examined and fleshed out for this version of the TRM and changes to testing methodologies that are currently underway in the HVAC industry (HSPF2) | Vaughn, Andrew C | 7/12 Working Group and 7/26 TAC focused on these measures. Draft 2 contains current standing on these issues. We will continue the conversations and try and reach consensus on all open issues. | None |  | Sam |  | N/A
3 | Ameren | 5.3.1 | 5.3.1 Air Source Heat Pump | 81 | installations | added redlines that the updated description should only apply to known installations, since programs do not know what additional heating is provided in a midstream program. | Vaughn, Andrew C | Discussed on TAC. Edits added. | Edits made |  | Sam |  | Y
3 | Ameren | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 89 | Heatin | Correct to "Heating" | Froio, Zach | Thank you. Fixed | Typo fixed | Not needed |  |  | N/A
3 | Ameren | 5.3.9 | 5.3.9 High Efficiency Bathroom Exhaust Fan | 154 | Defaults provided below | Note: It appears that all published default savings do not correlate with the actual calculated when using the table inputs. For example, Standard Usage ENERGY STAR kWh is 29.5, but the published is 28.9. And the default savings published for ENERGY STAR most efficient fan with continuous usage = 216.9. If the default values are entered into the savings formula, this results in 218.7 kWh and .0249 kW. May want to consider an errata? | Froio, Zach | This is a rounding issue - i.e. the variables in the TRM are rounded but actual average values are used to determine the savings. If you review the refence file "CEC Bath Fan" you can see the calculations being made. | None | Sam |  |  | N/A
3 | Ameren | 5.3.12 | 5.3.12 Ductless Heat Pumps | 172 | HeatLoadFactor | This new factor adds additional complexity to the measure for what appears to be little benefit to overall technical accuracy since so many assumptions needs to go into the table. We advocate that this factor should not be included at this time. | Vaughn, Andrew C | Discussed in working group and hopefully concerns have been realized. | Adjusted table order to be consistent with other tables (i.e. zone 1 to 5). Added unknown weighted averages. |  | Sam |  | Y
3 | Ameren | 5.3.12 | 5.3.12 Ductless Heat Pumps | 173 | 1 ton | Most units do not come in such discreet tonnage increments. The implementation of these tables would cause weighted averages to need to be used. Yet another reason that we feel these changes are overcomplicating an already complicated measure. | Vaughn, Andrew C | Table has been adjusted to provide tonnage ranges instead. | Columns are not tonnage ranges. |  | Sam |  | Y
3 | Ameren | 5.4.3 | 5.4.3 Heat Pump Water Heaters | 239 | kWh_cooling | UEF_new is used where it should be UEF_HPWHEFFICIENT. On p244, the same comment within the kWh_heating equation. Also, both of these kWh_cooling and kWh_heating should be changed to the new CoolingImpact and ElecHeatImpact variables. On p.246, the term "Location" should be changed to "Dwelling Unit". On p. 247, the section on mid-life adjustment should be removed. The HVAC interaction factors for this measure are 27% for coling and 5% for heating even before the 22% location factor adjustment. This level of complexity added onto this measure for such small fractions of savings seems prohibitively complicated. | Froio, Zach | Agree on updating variable names consistent with new terminology. Not sure where the "Location" term is. Upon discussion at TAC and review - agree that application of the mid-life adjustment for the HVAC efficiencies for this measure is unnecessary complication as this only relates to the small waste heat impact. Proposal to remove the mid-life adjustment and prescribe that the code minimum HVAC efficiencies should be assumed for all homes. | Updated variable names. All HVAC efficiency assumptions are now based on code minimum and the mid-life adjustment has been removed. | Sam |  | Propose removing mid-life… this is only measure that this is just about waste heat (tiny impact)… propose assuming default baseline efficiencies. | Y
3 | Ameren | 5.4.4 | 5.4.4 Low Flow Faucet Aerators 5.4.5 Low Flow Showerheads 5.4.8 Thermmosstatic Restrictor Shower Valve | 254 | Source ID | These are sources that seem to be from a TRM workpaper template. If those sources are used in the TRM entry, they should be identified in the footnotes of the entry. | Froio, Zach | While we agree this is an inconsistent format to the other measures, it has been this way for many years and we don't feel it necessitates a change at this time. | None | Not needed |  |  | N/A
3 | Ameren | 5.5.8 | 5.5.8 LED Screw Based Omnidirectional Bulbs | 311 | Equipment | AIC to provide redline here | Matthew Armstrong | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | Ameren | 5.5.8 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp 5.5.8 LED Screw Based Omnidirectional Bulbs 5.5.9 LED Fixtures | 311 | That being said, the availability and sales of equipment has been previously restricted by EISA has not been expediently changed following proposed timelines. | AIC Redline | Vaughn, Andrew C | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | Ameren | 5.5.8 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp 5.5.8 LED Screw Based Omnidirectional Bulbs 5.5.9 LED Fixtures | 311 | The lifetime of any measure however is reduced to two years for non-income eligible populations (representing the replacement of two incandescent/halogen bulbs in storage) and five years for income eligible populations. | Recommend deletion | Vaughn, Andrew C | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | Ameren | 5.5.8 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp 5.5.8 LED Screw Based Omnidirectional Bulbs 5.5.9 LED Fixtures | 311 | This v11 TRM can be used for non-income eligible programs including retail programs and kit programs up to 6/30/2023, and for income eligible programs through 2023, acknowledging that smaller store including discount and thrift stores may continue to sell non-compliant bulbs for some time (as observed following the first phase of EISA). Note all programs in DIY, Warehouse and Big Box stores should end 6/30/2023 including those in income eligible neighborhoods. The continuation of programs beyond 2023 should be reviewed during the v12 update cycle. Direct Install programs where it can be shown that the LED is replacing working inefficient lighting can also continue. The lifetime of any measure however is reduced to two years for non-income eligible populations (representing the replacement of two incandescent/halogen bulbs in storage) and five years for income eligible populations. | Recommend deletion and replace with "Due to the uncertainty in DOE enforcement and availability, the measure will not changed at this time. Each Program Administrators' Independent Evaluator will collect market data, starting July 1, 2023 through December 31, 2024, to demonstrate the point at which non-compliant bulbs are no longer available for purchase at retailers." | Vaughn, Andrew C | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | Ameren | 5.5.8 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp 5.5.8 LED Screw Based Omnidirectional Bulbs 5.5.9 LED Fixtures | 311 | The natural growth of LED market share however, has and will continue to grow over the lifetime of the LED measures installed. The TAC convened a Lamp Forecast Working Group to develop a forecast of the baseline growth of LED, based upon historical growth rates provided via CREED LightTracker data, comparisons of with and no-program states and review of projections provided by the Department of Energy.[1]This baseline forecast was then used to estimate how replacement lamps would change over the lifetime of an LED. A single mid-life adjustment is calculated that results in an equivalent net present value of lifetime savings as the forecast decline in annual savings. Income Eligible Program AdjustmentsThe Lamp Forecast Working Group also developed forecasts for estimated Income Eligible market growth in LEDs. These forecasts are used to provide a separate mid-life adjustment for programs supporting income eligible populations. Note that upstream lighting programs in DIY, Warehouse, and Big Box stores located in income eligible neighborhoods should not assume that all customers are from income eligible populations, as data has indicated that the product selection and low prices found in these stores attract customers from beyond.[1] A weighted blend of the two measure types (Income eligible and non-income eligible) can be used for DIY, Warehouse, and Big Box stores located in income eligible neighborhoods based upon primary evaluation research at these store types, or using a default of 30% income eligible customers.[1] | Recommend keeping | Vaughn, Andrew C | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | Ameren | 5.5.8 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp 5.5.8 LED Screw Based Omnidirectional Bulbs 5.5.9 LED Fixtures | 312 | New Construction programs should not include savings from this measure beyond 6/30/2023. | Recommend deletion | Vaughn, Andrew C | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | Ameren | 5.5.8 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp 5.5.8 LED Screw Based Omnidirectional Bulbs 5.5.9 LED Fixtures | 312 | However, The deemed measure life is 8 years for exterior application and lifetimes are capped at 10 years for other applications.[1]For early replacement measures, if replacing a halogen or incandescent bulb, the remaining life is assumed to be 333 hours. For CFL’s, the remaining life is 3,333 hours.[1]for all installations the measure life is assumed to be two years for non-income eligible populations (representing the replacement of two incandescent/halogen bulbs in storage) and five years for income eligible populations. | Recommend reverting to previous language | Vaughn, Andrew C | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | Ameren | 5.5.8 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp 5.5.8 LED Screw Based Omnidirectional Bulbs 5.5.9 LED Fixtures | 316 | Mid-Life Baseline AdjustmentDuring the lifetime of a standard Omnidirectional LED, the baseline incandescent/halogen bulb would need to be replaced multiple times. In December 2019, DOE issued a final determination for General Service Incandescent Lamps (GSILs), finding that the more stringent standards (45 lumen per watt) prescribed in the 2007 EISA regulation to become effective in 2020 (known as the ‘Backstop’ provision), was not economically justified. However, natural growth of LED market share has, and will continue to grow over the lifetime of the measure, and so a single mid-life adjustment is calculated that results in an equivalent net present value of lifetime savings as the forecast decline in annual savings. See ‘Lamp Forecast Workbook_2021.xls’ for details.The calculated mid-life adjustments for 2021 are provided below for each population:PopulationYear from which adjustment is appliedAdjustment Factor applied to Annual kWh SavingsIncome Eligible202981%All others202634% | Recommend reverting to previous language and updating adjustment factors similar to v10 of TRM | Vaughn, Andrew C | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | Ameren | 5.5.8 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp 5.5.8 LED Screw Based Omnidirectional Bulbs 5.5.9 LED Fixtures | 318 | For non-income eligible populations, no O&M costs should be applied.For income eligible populations, an annual baseline cost of $1 should be applied. In order to account for the natural growth of LED over the lifetime of the measure, an equivalent annual levelized baseline replacement cost is calculated and applied over the life of the measure as described above. The NPV for replacement lamps and annual levelized replacement costs using the societal real discount rate of 0.42% are presented below.[1] | Recommend reverting to previous language | Vaughn, Andrew C | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | Ameren | 5.5.9 | 5.5.9 LED Fixtures | 319 |  | For Task/Under Cabinet Lighting, the baseline lamp type would be consistent with linear fluorescent and would not be impacted by EISA. | Vaughn, Andrew C | Discussed at TAC. We have drafted a new "EISA Exempt LED Lighting" measure that can hold assumptions for any lamp or fixture that is exempt. For now this contains low and high lumen lamps and Linear Task/Under cabinet lighting. | Added new measure for EISA Exempt LED Lighting. |  |  |  | Y
3 | Ameren | 5.5.9 | 5.5.9 LED Fixtures | 320 | populations | Task/Under Cabinet lighting should continue with a 15 year measure life | Vaughn, Andrew C | See above | See above |  |  |  | N/A
3 | Ameren | 5.5.9 | 5.5.9 LED Fixtures | 323 | Adjustment | Mid Life Baseline Adjustment should not apply to Task/Under Cabinet Lighting | Vaughn, Andrew C | See above | See above |  |  |  | N/A
3 | Ameren | 5.7.3 | 5.7.3 Electric Vehicle Charger | 433 |  | kW savings should be near zero and likely slightly positive. The negative value listed is a carryover from when an elelctrical vehicle measure was proposed. Agree this needs to be an errata. | Vaughn, Andrew C | Agreed. VEIC have calculated new values in the v10 errata and updated values based on other v11 updates for v11. | v10 errata submitted and values updated again for v11. | Sam |  |  | Y
3 | ComEd | 5.1.7 | 5.1.7 ENERGY STAR and CEE Tier 2 Room Air Conditioner 5.1.9 Room Air Conditioner Recycling 5.1.13 Income Qualified: ENERGY STAR and CEE Tier 2 Room Air 5.3.1 Centrally Ducted Air Source Heat Pump 5.3.3 Central Air Conditioning 5.3.4 Duct Insulation and Sealing 5.3.8 Ground Source Heat Pump 5.6.6 Rim/Band Joist Insulation 5.6.9 Insulated Cellular Shades | 38 | Weighted Average[1]ComEdAmerenStatewide2262462485 | Please add a caveat that the TRM is not prescribing this weighted average be applied. Sometimes, for HVAC, we have used program-history-weighted average. Evaluators should apply what they think is best here and not be over-ridden by the TRM. | Mcnish, Rebecca K:(ComEd) | Agreed. Language added. | Added in footnote: "Alternative program-weighted assumptions can be used if appropriate." | Sam |  |  | Y
3 | ComEd | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump 5.3.3 Central Air Conditioning 5.3.8 Ground Source Heat Pump 5.3.12 Ductless Heat Pumps | 84 | New Federal Standards | Language is unclear when new standards become effective within the TRM specifically. “New Federal Standards affecting heat pumps become effective January 1, 2023.”“These new federal standards will be adopted by the program, beginning 1/1/2024.” | Mcnish, Rebecca K:(ComEd) | The federal standards become baseline in 1/1/2024. Following the TAC discussion we hope that any confusion is alleviated. | None | Jake | Sam |  | N/A
3 | ComEd | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump 5.3.12 Ductless Heat Pumps | 88 | Unknown Baselines Midstream Programs | It should not be assumed that all Midstream Programs have unknown baselines. Further, it should not be assumed that all unknown baseline conditions will only be in Midstream Programs. | Mcnish, Rebecca K:(ComEd) | OK language will be adjusted | Changed to: "Programs where existing system unknown (e.g. Midstream)" | Sam |  |  | Y
3 | ComEd | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump 5.3.8 Ground Source Heat Pump 5.3.12 Ductless Heat Pumps 5.4.3 Heat Pump Water Heaters | 99 | Cost effectiveness screening section | Is it still true after site energy calculations were prescribed in the legislation that there are 2 different savings calculations? | Mcnish, Rebecca K:(ComEd) | Yes. The fuel switch algorithms end up with a single MMBtu value that is converted to either electric or gas. For cost effectiveness screening the actual change in fuel (so reduced gas and increased electric) should be used and that is what is detailed in this section. Language revised to clarify. | Slight edits to language to clarify why this is neeeded. | Sam |  |  | Y
3 | ComEd | 5.5.6 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp 5.5.8 LED Screw Based Omnidirectional Bulbs 5.5.9 LED Fixtures | 305 | This v11 TRM can be used for non-income eligible programs including retail programs and kit programs up to 6/30/2023, and for income eligible programs through 2023, | The TRM should avoid prescribing outcomes of Program Administrator decisions on when to sunset programs. The TRM should state when baselines will change and for which customers and channels, and what the impact of those changes are on savings and lifetimes. | Mcnish, Rebecca K:(ComEd) | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | ComEd | 5.5.6 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp 5.5.8 LED Screw Based Omnidirectional Bulbs 5.5.9 LED Fixtures | 305 | and for income eligible programs through 2023, acknowledging that smaller store including discount and thrift stores may continue to sell non-compliant bulbs for some time (as observed following the first phase of EISA). | This v11 update does not fully reflect the likelihood of sell-through, which is based on actual experience, not a supposition that there will be robust enforcement. ComEd proposes savings continue for EISA impacted bulbs in income eligible retail and kit programs through at least 2025. This language already acknowledges non-compliant bulbs remained in smaller stores for some time after the first phase of EISA but fails to mention that “some time” is several years, and more than the additional six months granted here. | Mcnish, Rebecca K:(ComEd) | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | ComEd | 5.5.6 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp 5.5.8 LED Screw Based Omnidirectional Bulbs 5.5.9 LED Fixtures | 305 | The continuation of programs beyond 2023 should be reviewed during the v12 update cycle. | This approach creates uncertainty for utility planning purposes that may result in interruptions to impacted income eligible programs. Our proposal to continue savings for EISA impacted bulbs in income eligible retail and kit programs through 2025 at least addresses this concern for the Plan 6 period (2022-2025), though we anticipate non-compliant bulbs will be available in smaller stores beyond that based on actual experience. | Mcnish, Rebecca K:(ComEd) | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | ComEd | 5.5.6 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp 5.5.8 LED Screw Based Omnidirectional Bulbs 5.5.9 LED Fixtures | 305 | five years for income eligible populations. | For EISA impacted bulbs in income eligible retail and kit programs continued through 2025, we propose a 10-year measure life based a v10 assumptions, with the midlife adjustment year shifted as needed based on the installation year. | Mcnish, Rebecca K:(ComEd) | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | ComEd | 5.5.6 | 4.5.4 LED Bulbs and Fixtures 5.5.6 LED Specialty Lamp 5.5.8 LED Screw Based Omnidirectional Bulbs 5.5.9 LED Fixtures | 306 | (representing the replacement of two incandescent/halogen bulbs in storage) | This language seems unnecessary given an explanation is not provided for income eligible. This language is also not included in the commercial measure 4.5.4 LED Bulbs and Fixtures. | Mcnish, Rebecca K:(ComEd) | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 82 | electric baseline | Aren't there also scenarios where the electric baseline is resistance heat? The midstream weighted average efficiencies assume so, right? | Ted Weaver | This section relates to New Construction. We think its appropriate to assume ASHP for the electric baseline. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 83 | baselines | Aren't there also scenarios where the electric baseline is resistance heat? The midstream weighted average efficiencies assume so, right? | Ted Weaver | For Time of Sale, since the baseline is what is existing, then yes electric resistance is a reasonable baseline and will be added. | Added electric resistance with HSPF of 3.412 to table |  | Sam |  | Y
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 83 | e baselines provided below | This is confusing, because the baseline is a combination of a heating and cooling system. Suggest a 6 row X 3 column table instead:Rows:ASHPResistance Heat + CACGas/LP Furnace + CACGas/LP Boiler + CACOil Furnace + CACOil Boiler + CACColumns:Unit TypeBaseline Heating EfficiencyBaseline Cooling Efficiency (This would include both SEER & EER; or make a 4th column) | Ted Weaver | We don't think this is necessary (and has been in this format for many years). This table is simply providing the baseline for whatever HVAC systems are appropriate for the application.The midstream/unknown assumptions when coupled with the %Fuel Switch will result in the appropriate assumptions being applied. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 83 | Unknown (e.g. midstream)13.1 SEER, 10.5 EER, 5.44 HSPF, 80.1% AFUE | This is still confusing to us regarding how the average could be less than 14. Does this imply that there are a mix of RSH/CAC, ASHP, and Furnace/CAC? Seems like the math won't work right, i.e., the algorithm using weighted average inputs won't produce the same answer as the weighted average of the algorithm outputs. Especially with the fuel switching... | Ted Weaver | The assumptions for unknown provide the appropriate efficiency assumptions that, coupled with the %FuelSwitch, should be used if the existing system is unknown. So say we assume 10% are fuel switches - you would calculate electric savings using the 13.52 SEER and 6.3 HSPF assumptions (which reflect a mix of CAC, ASHP and resistance heat) * 90%, and then fuel switch savings using the 80.1% baseline (which reflect a mix of furnace and boiler) * 10%. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 83 | ASHP | This value needs a reference. | Ted Weaver | Added citation. | Added citation. |  |  |  | N/A
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 83 | actual costs should always be used for fuel switch measures | Does this imply that midstream participants are never fuel switch applications? | Ted Weaver | This is old language before midstream was added as an option for this measure. We propose removing this language and using the "unknown" additional installation costs that are now being provided. | Removed this sentence. |  | Sam |  | Y
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 84 | ASHP | Will there be a premium added to these for cold climate models? | Ted Weaver | The cost data used was mostly cold climate models or certainly a mix - so we do not believe a premium is warranted here. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 84 | 17+$7,286 + $600/ ton $1,381 / ton + $724 | These costs still seem low compared to the costs from the NAHB report.NAHB report uploaded to VEIC website along with cost comparison spreadsheet. | Ted Weaver | We reviewed this data and think that our proposed costs plus the default electrification cost is relatively consistent up to SEER 18 (and we prefer to use Illinois program data if available). However this NAHB data indicates potentially higher costs for the more efficient units. We have asked Ameren if they are able to split out by efficiency in these higher tiers. For this draft we have simply trended the costs upwards. | Higher efficiency assumptions trended from existing assumptions. |  | Sam |  | N/A
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 84 | 18$1,381 / ton + $724 | These should keep increasing to at least a SEER of 20. Seems like you could extrapolate from the first three tiers. | Ted Weaver | As above - we have asked Ameren to see if they can split data further. For this draft we have simply trended the costs upwards. | Higher efficiency assumptions trended from existing assumptions. |  | Sam |  | N/A
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 84 | Fuel switch scenarios are likely to require additional installation work | Above you said that the cost values don't apply to fuel switch, and that actual costs should be used instead. Unclear how you could then add $1K for fuel switch... | Ted Weaver | Agreed- as above we think the old language should be removed. | Original sentence removed. |  | Sam |  | Y
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 84 | adding new electrical circuits, capping existing gas lines and upgrading electrical panels | Removal costs should be included | Ted Weaver | We are awaiting SlipStream's assessment of the appropriate additional costs here. Presumably removal costs are required for any old system and so its not clear this would be a significant difference. | None |  | N/A |  | N/A
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 84 | 1000 | The NAHB report has ~$2,000 for panel upgrades itself. | Ted Weaver | We are awaiting SlipStream's assessment of the appropriate additional costs here. Not all installations are going to need this upgrade so we are trying to reflect an average. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 87 | 9.3 | Since the federal standard has been SEER 10 since 1992, it seems odd that the baseline efficiency is only 9.3. In any case, six more years of new CA installations have occurred since the study was completed. If you eliminated the oldest units from the 2018 study sample (with SEERs probably around 8) and replaced them with newer units (SEERs above 13 ), then the average would increase by at least 2 SEER points. | Ted Weaver | Upon review and discussion with Opinion Dynamics, proposal is to increase existing SEER assumption to 9.7, HSPF to 5.78 and EER to 7.83 based on footnotes provided in the 2018 study. | Assumptions updated |  | Sam |  | Y
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 87 | FLH_ASHPheat | See Nicor comments and spreadsheet emailed to Sam Dent on 7/14. These values are too high given actual heating loads in IL. They were developed by applying a (very small) 3 ton HP to the gas load for an average IL household. Using a more realistic heating capacity would drop them close to the 973 hours (for Chicago) used in the furnace algorithm.In any case, FLH assumptions should be consistent across furnace, ASHP, and DMSHP algorithms. All assume property sized equipment. | Ted Weaver | Smaller capacity heat pumps and higher EFLHs are to be expected. Heat pumps run longer at lower discharge temperatures to meet loads. The HSPF rating accounts for back up resistance heat during hours when the Heat Pump could not meet the heating load, and units are tested within Zone 4, consistent with most of Illinois. The HP EFLH * average capacity is largely consistent with the furnace EFLH * average capacity. We can understand your argument IF the average homes getting a centrally ducted ASHP were significantly smaller than the average furnace heated home. However, data we have seen does not support that conclusion. Finally, the only time the single family EFLHs have been tested against metered data (Opinion Dynamics/Cadmus 2018 Residential HVAC Metering Study) they were found to be reasonable. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 88 | 5.54[1] | Same comment as for SEER values.- Seems too low, even for 2018 analysis.- 6+ more years of replacements with higher standards have occurred since 2018 analysis. | Ted Weaver | Upon review and discussion with Opinion Dynamics, proposal is to increase existing SEER assumption to 9.7, HSPF to 5.78 and EER to 7.83 based on footnotes provided in the 2018 study. | Assumptions updated |  | Sam |  | Y
3 | Nicor Gas | 5.3.1 | 5.3.1 Centrally Ducted Air Source Heat Pump | 89 | Early Replacement (Remaining useful life of existing equipment)[1] | Same comment as above re: baseline efficiencies. This study was completed ~15 years ago... | Ted Weaver | Upon review and discussion with Opinion Dynamics, proposal is to increase existing SEER assumption to 9.7, HSPF to 5.78 and EER to 7.83 based on footnotes provided in the 2018 study. | Assumptions updated |  | Sam |  | Y
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 166 | If the efficiency of the existing unit is less than the maximum shown below, the Baseline efficiency is the actual efficiency value of the unit replaced. If the efficiency is greater than the maximum, the Baseline efficiency is shown in the “New Baseline” column below: | This is confusing. Is there a reason that we don't just use the existing unit actual value, like for ASHP? | Ted Weaver | We believe this was set up in this way to try and only claim higher savings for early replacement when the installation is being done for efficiency reasons as opposed to for convenience/ additional cooling etc. Thus if the replacement unit is above a threshold we are effectively treating it as a time of sale application. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 166 | Existing SystemMaximum efficiency for ActualNew Baseline[1] | See comment above for ASHP, suggesting explicitly identifying combinations of heating and cooling. And adding value for resistance heat baseline.(It's trickier here because you have 2 columns of data…) | Ted Weaver | See above - we don't believe this is necessary. | Added electric resistance with HSPF of 3.412 to table |  | Sam |  | Y
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 166 | 13 SEER | Does this need an EER value? | Ted Weaver | Agreed. Added. | Added EER to CAC row. |  |  |  | N/A
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 167 | baselines provided below | This is confusing, because the baseline is a combination of a heating and cooling system. Suggest a 6 row X 3 column table instead:Rows:ASHPResistance Heat + CACGas/LP Furnace + CACGas/LP Boiler + CACOil Furnace + CACOil Boiler + CACColumns:Unit TypeBaseline Heating EfficiencyBaseline ooling Efficiency (This would include both SEER & EER; or ake a 4th column) | Ted Weaver | See above - we don't believe this is necessary. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 167 | Unit TypeEfficiency Standard | Confused as to why there are two tables; one on previous page and this one with virtually the same data. | Ted Weaver | As above, the table above is relating to appropriate baselines to only claim early replacement savings for units that are being replaced for efficiency reasons. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 167 | Unit TypeEfficiency Standard | See comments for ASHP regarding table structure. And need to add resistance heat baseline. | Ted Weaver | See above - we don't believe this is necessary although we have added the electric resistance baseline. | Added electric resistance with HSPF of 3.412 to table |  | Sam |  | Y
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 168 | Full Install Cost ($/ton)[1] | Seems like these values should be updated to include inflation from the 2016/2017 values documented in the source document. | Ted Weaver | This would be true of many costs in the TRM and its not always true that costs follow inflation. We asked if Ameren has any reasonable data on costs for comparison but their dataset is very limited. Suggest this might be an area of analysis in a future year. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 168 | 2041 | These values seem low compared to ASHP. 4 ton HSPF 10.5 (SEER ~18) comes in at ~$6,400 for ductless and ~$9,700 for ducted. | Ted Weaver | We do not have any data to support an update at this time. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 168 | (including any necessary electrical or distribution upgrades required | The paragraph from the ASHP workpaper regarding additional costs for electric line extension, electric panel upgrades, and gas line capping should be added here. | Ted Weaver | Agreed. Same language and placeholder value added. | Language added |  | Sam |  | Y
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 171 | EFLHcool | Similar to comments on heating FLH, its difficult to understand why a propery sized ductless system would have different FLH than a properly sized ASHP. | Ted Weaver | From Guidehouse: The source footnote concurs that additional metering in single family residences is recommended. But in both chapters the values are derived from actual metering studies. Centrally ducted and ductless could have different use cases. Additionally, the EFLH term (both heating and cooling) compensates for the system's performance curve as a function of temperature. Significant differences in the performance curves would affect the EFLH. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 172 | Early Replacement | Same comment as made above for ASHP. These values seem too low in general and need to be updated for the 6+ years of higher efficiency equipment installed since the reference source was completed.This comment applies to the room AC values as well. | Ted Weaver | Upon review and discussion with Opinion Dynamics, proposal is to increase existing SEER assumption to 9.7, HSPF to 5.78 and EER to 7.83 based on footnotes provided in the 2018 study. | Assumptions updated |  | Sam |  | Y
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 172 | EFLHheat | See comments on FLH for ASHP.See email and spreadsheet sent to Sam Dent on 7/14. | Ted Weaver | As above. | None |  | Sam
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 172 | HeatLoadFactor | These heat load factors are problematic:As we understand it, they keep the size of home constant at 2,500 sf and then determine how much of the entire home heating load can be carried by the DMSHP. Basically, this measures how much each HP is over/undersized for a 2,500 sf home.So:- What happens if customer installs a 1.5 ton HP in a 800 sf apartment? Or a 10,000 sf mansion? Do you still apply these adjustment factors?- What happens if a customer installs 4 1-ton HPs? Do you still apply these adjustment factors? Or do you apply the 4 ton factor?- What happens if a customer installs a 1.5 ton HP in the master bedroom of a 4,000 sf home? Or a 1 ton unit in a spare room in the corner? Do these tables assume that they would run the heat pump to keep the living room warm on a chilly October day?- What happens if a customer uses simultaneous operation, but the HP thermostat is not set 2 degrees higher?- There are probably more issues with using these appropriately in implementation... | Ted Weaver | From Guidehouse: ComEd's research into how DMSHPs are being used showed that there are indeed a lot of use cases. These tables were developed using a model of an average sized home as a representative average. In partial displacement scenarios, if controls are programmed accordingly (ex. 1st table), the models shows that the heat pump is able to provide a higher heat load than the current TRM algorithm (EFLH x capacity) reflects. If the controls are switching to back up heat at a moderate temperate (ex. 2nd table), then the models show the heat pump will not provide the (EFLH x capacity) heat load, thus the factors are mostly <1. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 172 | HeatLoadFactor | Continued from above |  | From Guidehouse: - What happens if customer installs a 1.5 ton HP in a 800 sf apartment? Or a 10,000 sf mansion? Do you still apply these adjustment factors? For midstream you would use the Unknown values which are a weighted average of the most prevalent cases found in the survey results If in a downstream program you know it is full displacement such as with the small condo then you would use 1.0. If you know the type of partial displacement for the mansion you would use the corresponding adjustment factor. - What happens if a customer installs 4 1-ton HPs? Do you still apply these adjustment factors? Or do you apply the 4 ton factor? The factor is based on the outdoor compressor size so you would use the 4 ton factor that is most appropriate based on the amount of information collected as part of the program. - What happens if a customer installs a 1.5 ton HP in the master bedroom of a 4,000 sf home? Or a 1 ton unit in a spare room in the corner? Do these tables assume that they would run the heat pump to keep the living room warm on a chilly October day? There are many different potential options for installation. We considered the most prevalent cases from the survey for developing these tables and for determining the weights. The TRM is not intended to model every possible situation, but an average case. - What happens if a customer uses simultaneous operation, but the HP thermostat is not set 2 degrees higher? The TRM approach is not intended to model all possible cases. - There are probably more issues with using these appropriately in implementation... As stated above, the goal of the TRM is to develop a deemed method that best represents the average or most prevalent cases, not all possible cases. | None |  |  |  | N/A
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 172 | HeatLoadFactor | Continued from above |  | VEIC: We think making it clear that the capacity used in the algorithm should be total capacity of all units installed in the home (not individual units) would be helpful. Note we have also added ComEd, Ameren and Statewide weighted average assumptions to these tables. | Clarification made. Weighted averages added |  |  |  | Y
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 174 | HeatLoadFactor_Gas | The note says that these values are weighted averages based on Guidehouse survey responses. We assume the weights are of the values in the previous three tables, But then why aren't the values in the middle of the ranges of the values in the three tables? These area all lower than any number in the above tables… | Ted Weaver | From Guidehouse: Survey responses indicated a portion of respondents weren't using their DMSHPs for heating (cooling only). Another portion fully displaced their previous system. These cohorts are weighted in with the partial displacement conditions in the unknown scenarios. | None |  | Sam |  | N/A
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 174 | HeatLoadFactor_Elec | Same issue here. | Ted Weaver | As above. | None |  | Sam
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 174 | Early Replacement (Remaining useful life of existing equipment) | Same comment as made for ASHP and for cooling baselines above. These values seem too low in general and need to be updated for the 6+ years of higher efficiency equipment installed since the reference source was completed. | Ted Weaver | Upon review and discussion with Opinion Dynamics, proposal is to increase existing SEER assumption to 9.7, HSPF to 5.78 and EER to 7.83 based on footnotes provided in the 2018 study. | Assumptions updated |  | Sam |  | Y
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 175 | Early Replacement (Remaining useful life of existing equipment)[1] | Same comments as above re: outdated baseline efficiencies. | Ted Weaver | Upon review and discussion with Opinion Dynamics, proposal is to increase existing SEER assumption to 9.7, HSPF to 5.78 and EER to 7.83 based on footnotes provided in the 2018 study. | Assumptions updated |  | Sam |  | Y
3 | Nicor Gas | 5.3.12 | 5.3.12 Ductless Heat Pumps | 178 | Early Replacement | Same comment as above re: outdated baseline assumptions. | Ted Weaver | Upon review and discussion with Opinion Dynamics, proposal is to increase existing SEER assumption to 9.7, HSPF to 5.78 and EER to 7.83 based on footnotes provided in the 2018 study. | Assumptions updated |  | Sam |  | Y
3 | Resource Innovations | 5.3.16 | 5.3.16 Advanced Thermostats | 198 | 20777 | Updated Elec_Heating_Consumption on Advanced Thermostats to 20,777 to match the Programmable Thermostat lookup table. Calculated as 834 divided by 0.03412 and reduced by 15% as explained in the footnote. | Haley Keegan | Agreed. Fixed. | Value updated | Not needed |  |  | Y
3 | Opinion Dynamics | 5.4.3 | 5.4.3 Heat Pump Water Heaters | 240 | [1] | Link to this study is now available and can be added to the footnote:https://ilsag.s3.amazonaws.com/AIC-Market-Effects-2021-HPWH-Market-Characterization-Report-FINAL-2021-09-15.pdf | Zachary Ross | Evaluation has been added to the reference folder. | Reference document added to folder. | Not needed |  |  | N/A
3 | Opinion Dynamics | 5.6.6 | 5.6.6 Rim/Band Joist Insulation | 415 | 1 | Need to insert ‘ΔTherms' here on the other left side of the equal sign in this equation. | Alex Caratti | Agreed. Done | Term added. | Not needed |  |  | N/A
3 | ICC | LED | LEDs |  |  | ICC provided comments captured here: https://portal.veic.org/projects/illinoistrm/Shared%20Documents/Technical_TRM_Effective_010123_Version_11.0/Draft%201%20Full%20TRM%206_24_22/Stakeholder%20Comments/TRM%20V11%20ICC%20Staff%20comments.docx?Web=1 | David Brightwell | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
3 | Ameren | LED | LEDs |  |  | Ameren provided additional comments captured here: https://portal.veic.org/projects/illinoistrm/Shared%20Documents/Technical_TRM_Effective_010123_Version_11.0/Draft%201%20Full%20TRM%206_24_22/Stakeholder%20Comments/Ameren%20Illinois%20Position%20-%20TRM%20v11%20Lighting%20Measure%20proposal.docx?Web=1 | AIC | In light of alternative proposal being drafted and discussions continuing, we are not providing a response to LED Lighting comments. | None |  |  |  | N/A
4 | Enervee | 6.3.1 | 6.3.1 Efficient Choice |  |  | Enervee submitted comments to the IL TRM SharePoint site, that can be accessed here: https://portal.veic.org/projects/illinoistrm/_layouts/15/WopiFrame.aspx?sourcedoc=/projects/illinoistrm/Shared%20Documents/Technical_TRM_Effective_010123_Version_11.0/Draft%201%20Full%20TRM%206_24_22/Stakeholder%20Comments/7-15-22%20-%20Enervee%20TRMv11%20Comments%20(Efficient%20Choice).docx&action=default | Christopher Healey | Opinion Dynamics met with Enervee, Verdant and other key stakeholders and have developed a second draft of the measure. There remain a few open items that may result in changes in Deliverable 3. | New version provided |  | Zach |  | Y
4 | Verdant Associates | 6.3.1 | 6.3.1 Efficient Choice | 2 | Purchase Rates | General Comment.The TRM workpaper should give a single definition for purchase rate, rather than splitting it into four parts. These are four different ratios that could have their ouwn definition. We suggest adding an equation for purchase rate to help clarify the verbal description. | Ethan Barquest | Opinion Dynamics met with Enervee, Verdant and other key stakeholders and have developed a second draft of the measure. There remain a few open items that may result in changes in Deliverable 3. | New version provided |  | Zach |  | Y
4 | Verdant Associates | 6.3.1 | 6.3.1 Efficient Choice | 2 | and each utility’s ECT. | Clarifying that ECT purchase rate research is utility specific. For example Ameren and ComEd should have distinct purchase rates | Ethan Barquest | Opinion Dynamics met with Enervee, Verdant and other key stakeholders and have developed a second draft of the measure. There remain a few open items that may result in changes in Deliverable 3. | New version provided |  | Zach |  | Y
4 | Verdant Associates | 6.3.1 | 6.3.1 Efficient Choice | 2 | The targeted confidence and precision for purchase rates should also be determined by the evaluator. | Additions related to precision, grouping of like appliances and how rebated savings should be account for. | Ethan Barquest | Opinion Dynamics met with Enervee, Verdant and other key stakeholders and have developed a second draft of the measure. There remain a few open items that may result in changes in Deliverable 3. | New version provided |  | Zach |  | Y
4 | Verdant Associates | 6.3.1 | 6.3.1 Efficient Choice | 2 | easures purchased with utility rebates, their associated energy, demand, water and natural gas savings should be claimed by the program incentivizing the measure. Savings from measures receiving rebates should not be claimed by the ECT as detailed in the purchase rate section above. | Clarifying how rebated measures should be handled with respect to the ECT | Ethan Barquest | Opinion Dynamics met with Enervee, Verdant and other key stakeholders and have developed a second draft of the measure. There remain a few open items that may result in changes in Deliverable 3. | New version provided |  | Zach |  | Y

## Draft 2
Volume | Stakeholder Organization | Measure # | Measure | Page | Comment scope | Comment text | Author | VEIC Response | Changes made
2 | Ameren | 4.4.15 | Single Package and Split System Unitary Air Conditioners | 329 | Current Code minimum | Suggest language similar to 4.4.9 “In order for this characterization to apply, the baseline equipment is assumed to meet the efficiency requirements within the IECC code in effect on the date of the building permit (if unknown assume IECC 2018).” | Vaughn, Andrew C. | Language in both measures updated to refer user to appropriate code in effect at the municipality. | Language updated.
2 | Ameren | 4.4.15 | Single Package and Split System Unitary Air Conditioners | 329 | Code Effective Date | Energy codes working group to discuss whether small commercial can wait adoping until 2024 | Vaughn, Andrew C. | We have added language to the effect that if evaluation determines that the new code is not appropriate due to supply constraints or other issues that the previous code level can be assumed as baseline through 2023. | Language added.
2 | Ameren | 4.4.59 | Ductless Heat Pumps | 612 | HeatLoadFactor | These values are lower than the modeling that we have done. We will provide the alternative modeling for review | Vaughn, Andrew C. | Ameren and Guidehouse discussed many items in relation to this proposal and determined to keep as is for this year and revisit the assumptions again next year. | None
2 | Ameren | 4.4.59 | Ductless Heat Pumps | 613 | If Partial Displacement and Switchover at ≤24°F, HeatLoadFactor | Suggest a lower temperature cutoff | Vaughn, Andrew C. | Ameren and Guidehouse discussed many items in relation to this proposal and determined to keep as is for this year and revisit the assumptions again next year. | None
2 | Ameren | 4.4.59 | Ductless Heat Pumps | 614 | If Unknown, assume HeatLoadFactor_Elec: | Believe these are not appropriate based on Ameren Illinois customers. Currently trying to get information on how these were established | Vaughn, Andrew C. | After TAC discussion, unknown tables have been removed and replaced with language that evaluation should inform appropriate weighting of the various scenarios. | Unknown tables removed and new language on evaluation added.
2 | Nicor | 4.4.3 | Process Boiler Tune-Up | 249 | Measure Cost | Please refer to the provided data from Nicor Gas EE program. The average cost is $0.60/MBH with some outliers. However, about 70% of the reported costs was in around $0.50/MBH | Rohith Mannam | Thank you. Updated to $0.60 | Cost updated
3 | Nicor | 5.3.1 | Centrally Ducted Air Source heat pumps | 94 | Unknown (e.g. midstream)[1] | Ameren comments indicated that midstream participants are not necessarily unknown. | Ted Weaver | The "(e.g. midstream)" has been removed from all the unknown labels. | (e.g. midstream) removed
3 | Nicor | 5.3.1 | Centrally Ducted Air Source heat pumps | 95 | Electrification Cost | We look forward to reviewing the Slipstream cost analysis. | Ted Weaver | Discussed in working groups - final placeholder of $2000 is added for central HP. We hope this will be refined in future iterations. | $2000 default added
3 | Nicor | 5.3.1 | Centrally Ducted Air Source heat pumps | 100 | EFLH heat | We continue to believe that these are unsupported and biased high:- They were created with a back of the envelope calculation using unsupported assumptions, especially the assumption that "a typical 36,000 Btu/hr ASHP " heat pump would replace the "average gas heating load".- If the original calculation had guessed 4 tons instead of 3 tons, statewide FLH would drop from 1,821 to 1,350.- Sam Dent's analysis of Ameren data shows average home size of ~1,500 sf. Nicor's program data shows average home size of ~2,300 sf, or a difference of around 53%. Sam's regression analysis indicates that, for Ameren, this would increase capacity to ~40 kBtu/hr.- Ameren data covers southern Illinois, which has a design temperature of around 0. Design temperatures in Northern Illinois (which dominate the statewide weighted averages) are around -10. The difference in delta T (assuming heat pumps are sized to 47 degrees) is around 21%.- Factoring both of these into consideration would increase a "typical 36,000 Btu/hr ASHP" to around 48,000 Btu/hr. - Again, this would lead to a statewide FLH of 1,350.- This is also very close to the statewide ductless ELFH of 1,374. | Ted Weaver | As discussed, we feel there are ways to consider the data available to us that can both support and dispute the current EFLH assumptions. VEIC's latest version finds that when using the current TRM EFLHs together with program data for capacity and house size, that Ameren's average heat pump heated home requires 28,931 BTU/sq ft, compared to Nicor's average furnace heated home requiring 34,372 BTU/sq ft. The difference (16%) is reasonable compared to the expected climate driven difference (estimated at 13% using HDD assumptions or 15% using the delta T approach). If anything the HP numbers come out lower than you might expect. Our conclusion is that we do not yet have any solid data upon which to update these assumptions and since the only independent evaluation to test them found no significant difference, we feel that these should remain until new evaluation results are provided. We will add to the evaluation recommendation memo to this effect. | None
3 | Nicor | 5.3.12 | Ductless Heat Pump | 182 | Ductless Heat Pumps | See also comments on ASHP measure. | Ted Weaver | N/A | N/A
3 | Nicor | 5.3.12 | Ductless Heat Pump | 183 | Existing System | This needs the addition of resistance baseline made for ASHP above. | Ted Weaver | This table is providing the maximum efficiencies in order for the measure to be considered an early replacement. We don't think this is relevent to resistance. We did add it as a viable baseline to the table in the "Definition of Baseline Equipment" section. | None
3 | Nicor | 5.3.12 | Ductless Heat Pump | 185 | Electrification Cost | We look forward to reviewing the Slipstream analysis. | Ted Weaver | Discussed in working groups - final placeholder of $300 is added for ductless HP. We hope this will be refined in future iterations. | $300 default added
3 | Nicor | 5.3.12 | Ductless Heat Pump | 191 | HeatLoadFactor | We continue to believe that these adjustment factors are inappropriate for many installations, because they were developed assuming a 2,500 sf home, while many installations will be in smaller/different applications. We suggest that the following requirements be placed on the use of these factors:- Program administrators are required to collect square footage data for all installations (if possible).- These factors only be applied to installations in homes between 2,000 and 3,000 sf. | Ted Weaver | Upon TAC discussion, decision to leave values in but look to evaluation to help refine these assumptions in a future year. | None
3 | Ameren | 5.1.4 | ENERGY STAR Dishwasher | 24 | kWh Savings | The savings table was not updated to reflect default value for % Electric DHW/%Fossil Fuel DHW. | Froio, Zach | Thank you, updated using unknown location and building type assumption. | Values updated
3 | Ameren | 5.1.4 | ENERGY STAR Dishwasher | 27 | kW Savings | The savings table was not updated to reflect default value for % Electric DHW/%Fossil Fuel DHW. | Froio, Zach | Thank you, updated using unknown location and building type assumption. | Values updated
3 | Ameren | 5.3.1 | Centrally Ducted Air Source heat pumps | 100 | Unknown efficiencies | Opinion Dynamics to provide new values | Vaughn, Andrew C. | Final unknown efficiencies have been provided by Opinion Dynamics and Guidehouse. | Values updated
3 | Ameren | 5.3.1 | Centrally Ducted Air Source heat pumps | 104 | Example calcs | All base values (SEER_base, HSPF_base, EER_base) in the example calculations need to be updated to the revised published values. Revise example calculations to use the HSPF_ClimateAdj multiplier. | Froio, Zach | VEIC held off updating the example calcs until all assumptions are finalized. We have now updated the calculations in the almost final. | Example calculations updated
3 | Ameren | 5.3.8 | Ground Source Heat Pump | 158 | Example calcs | All base values (SEER_base, HSPF_base, EER_base) in the example calculations need to be updated to the revised published values. Revise example calculations to use the HSPF_ClimateAdj multiplier. | Froio, Zach | VEIC held off updating the example calcs until all assumptions are finalized. We have not updated the calculations. | Example calculations updated
3 | Ameren | 5.3.9 | High Efficiency Bathroom Exhaust Fan | 170 | Default Savings | Confirm the published values based on the default inputs defined in the TRM. For example, Standard Usage ENERGY STAR kWh is 29.5, but the published is 28.9. And the default savings published for ENERGY STAR most efficient fan with continuous usage = 216.9. If the default values are entered into the savings formula, this results in 218.7 kWh and .0249 kW. | Froio, Zach | This is a rounding issue - i.e. the variables in the TRM are rounded but actual values are used to determine the savings. If you review the reference file "CEC Bath Fan" you can see the calculations being made. | None
3 | Ameren | 5.3.12 | Ductless Heat Pump | 182 | Ductless Heat Pumps | Similar to C&I comment "HeatLoadFactor values are different the modeling that we have done. We will provide the alternative modeling for review" and "Suggest a lower temperature cutoff" and "Believe these are not appropriate based on Ameren Illinois customers. Currently trying to get information on how these were established" | Vaughn, Andrew C. | Ameren and Guidehouse discussed many items in relation to this proposal and determined to keep as is for this year and revisit the assumptions again next year. | None
3 | Ameren | 5.3.12 | Ductless Heat Pump | 191 | HeatLoadFactor | Heat loads were modeled based on a 2,500 sqft home, which is significantly larger than the average AIC DMSHP participant’s home (~1783 sqft), the state average sized home (~1632 sqft), and by extension, the average sized home in the ComEd service area. This may impact the share of the load a DMSHP unit can serve for partial displacement scenarios. A DMSHP unit would conceivably be able to serve a larger percentage of the heating load in a smaller conditioned space. | Froio, Zach | Ameren and Guidehouse discussed many items in relation to this proposal and determined to keep as is for this year and revisit the assumptions again next year. | None
3 | Ameren | 5.3.12 | Ductless Heat Pump | 192 | If Unknown, assume HeatLoadFactor_Gas:[1] | The 2022 survey suggests a significantly higher percentage of cooling-only DMSHP usage (36%), compared to 2014 (25%) and 2017 (11%) survey responses. The previous year trends suggest cooling-only usage should be lower, and Guidehouse notes “that percentage is likely to drop with programmatic and implementation improvements.” If the cooling-only usage is lower than the 2022 results suggest, the HeatLoadFactor should be higher than what is currently proposed. Guidehouse weights the unknown HeatLoadFactor by the number of survey respondents between with three DMSHP heating types: “none, partial displacement, and all”. Are these weights and resulting unknown HeatLoadFactors consistent with the %FuelSwitch factors for midstream programs, where savings are already apportioned between fuel switch and non-fuel switch scenarios? | Froio, Zach | After TAC discussion, unknown tables have been removed and replaced with language that evaluation should inform appropriate weighting of the various scenarios. | Unknown tables removed and new language on evaluation added.
3 | Ameren | 5.5.13 | EISA Exempt LED Lighting | 381 | LED New and Baseline Assumptions Table | The Ameren implementation team is looking at additional categories that need to be added. | Froio, Zach | We added T-LEDs in this "Almost Final" deliverable. | Added T-LEDs
3 | Ameren | 5.7.1 | High Efficiency Pool Pumps | 476 | Savings | Confirm the published values based on the default inputs defined in the TRM. For instance, TOS/Retrofit kWh savings for in ground pools published 307.7/1512.1 and when the inputs are put into the formulas 316.2/1483.2. | Froio, Zach | This is a rounding issue - i.e. the variables in the TRM are rounded but actual values are used to determine the savings. If you review the reference file "IL TRM_Pool Pump Calculator" you can see the calculations being made. Note we have increased to two decimal places the WEFbase variable which brings the resulting savings closer. | Increased WEFbase to 2 decimal places.
3 | ComEd | 5.3.1 5.3.8 5.3.12 | Centrally Ducted Air Source Heat Pump Ground Source Heat Pump Ductless Heat Pump | 99 | Existing system efficiencies | The average efficiencies of existing HVAC equipment in Illinois homes is constantly improving over the years as more efficient newer equipment replaces less-efficient older equipment. Therefore, the assumed efficiency of equipment replaced early should be reviewed periodically to determine if changes should be made. This review should consider all HVAC measures. Further, to determine if changes are warranted, a consistent criteria should be applied across all HVAC measures. ComEd believes a thorough review of all efficiency assumptions for existing HVAC equipment should be performed, but it must be done across the board and not just for selected equipment. If this all-HVAC review can be completed for this version of the TRM, ComEd supports the update. If not, it should be done next year in a comprehensive and consistent manner. | Mcnish, Rebecca K:(ComEd) | As discussed, this was based on a review of all HVAC equipment existing efficiencies. The recommendation was made by Opinion Dynamics to increase the Heat Pump efficiencies based on recommendations provided in the referenced evaluation. For gas equipment the existing assumptions were tested during an IQ specific analysis performed this year which found the existing assumptions to be very accurate. Further because there has been very little movement in efficiency standards of this equipment type there is less reason to believe the assumptions would change significantly. | None
4 | ComEd | 6.2.1 | Voltage Optimization | 31 | Review Deadline | ComEd recommends a review deadline of 1/1/2028, or the longest interval between review deadlines permitted, as no further changes are expected once update is finalized for TRM v11.0. | Mcnish, Rebecca K:(ComEd) | OK updated. | Review deadline updated
4 | ComEd | 6.2.1 | Voltage Optimization | 31 | Reconvening working group | In agreement with Guidehouse, a pledge to reconvene the working group is not necessary, in case there are no proposed changes in the future. Whether a working group is needed can be determined at a later date as part of the reliability review. | Mcnish, Rebecca K:(ComEd) | Removed the second sentence relating to reconvening a working group. | Sentence removed.
4 | Guidehouse | 6.2.1 | Voltage Optimization | 22 | will not include any provisions for recalculations of energy savings or CVR factor | As shown in the algorithm below, VO savings are calculated based on kWh_base*deltaV*CVR_f. While deltaV (the change in voltage) is likely to be fairly stable over time, Guidehouse would like to raise the fact that the other two inputs may not remain stable over a period of 50 years.kWh_base is the baseline load on a feeder. This can change over time, for example, as customers are added to or removed from a feeder or as individual customer loads change. Over time load on a given feeder could increase or decrease leading to higher or lower savings.e CVR factor likely changes over time as well. As noted in Guidehouse’s supporting documentation when this measure was initially introduced to the TRM, “there is no reason to believe that the CVRf is a constant over time. The relationship between voltage and energy reduction depends heavily on the mix of end-use loads being supplied with power, which changes over time. For example, one change that has occurred in the recent past is the shift from incandescent lightbulbs to LEDs. An expected change in the near future is increased levels of distributed energy resources such as solar and wind. There may well be other changes that we are unable to predict.” The CVRf could increase or decrease over time leading to higher or lower savings.Guidehouse raises this for stakeholders’ knowledge in considering the measure life extension. If stakeholders are ok with the proposal to renew the measure life every 15 years (up to 50) with the same savings we will agree to that consensus. However, another option would be to recalculate savings when the measure is renewed every 15 years (up to 50). This does raise uncertainty for the utilities both in what the savings would be and the method that would be used to claim them. The methods currently in the TRM would not be suitable since VO would not be cycling on and off (for the ComEd method) nor would there be a recent period without VO-enabled (for the Ameren method). One possibility would be to use the deemed CVRf in the TRM when savings are being reclaimed (e.g., the 2033 TRM) which could be updated over time through the TRM update process – for example literature reviews could be done or a subset of feeders could have VO cycling to allow for CVRf estimation, and the same change in voltage from when the feeder was first claimed (which assumes the voltage change is stable). That would leave the question of calculating the kWh baseline. This could be reviewed for trends over the 15 year period to see if it has substantially changed. | Carly Olig | After TAC discussion, Lifetime section updated to remove language about not recalculating energy savings after the 15 year period and replaced with language relating to the possible development of a new measure providing greater savings in the future. | Lifetime section updated.
4 | Guidehouse | 6.2.1 | Voltage Optimization | 22 | That is, the renewal would claim the same savings as the original measure for an additional 15 years (up to a maximum of 50 years) after verifying that VO is still operational on the feeder. | Recommend this sentence for additional clarity if no adjustments to savings are to be made at the time of renewal. | Carly Olig | As per above this is no longer relevent. | None
4 | Guidehouse | 6.2.1 | Voltage Optimization | 30 | Consistent | Recommend removing this language so that we do not need to convene a working group to fulfill this language if no changes are being proposed. | Carly Olig | Removed the second sentence relating to reconvening a working group. | Sentence removed.
Errata Memo | Guidehouse | 3.13 | Electrification and Fossil Fuel Baselines | 4 | Calculation set up | From Ryan Knoll Driftless Energy: Currently the TRM calculates the savings for electrification measures as a single step (baseline gas equipment compared to high efficiency electric equipment). For example in the centrally ducted air source heat pump section the fuel switch savings are calculated: FuelSwitchSavings = GasHeatReplaced – ASHPSiteHeatConsumed My question is if the full fuel switch savings should be considered electrification savings or if a two-step approach to divide the fuel switch savings into “electrification” savings and “traditional” savings is appropriate as shown below: FuelSwitchSavings (kWh) = Electrification Savings + Traditional EE Savings Electrification Savings (kWh) = Gas Heat Replaced – Code Compliant ASHP Site Heat Consumed Traditional EE Savings (kWh) = Code Compliant ASHP Site Heat Consumed – Actual Installed High Efficiency ASHP Site Heat Consumed Note that this does not change the total kWh savings attributed to the project. However, it does impact what portion of the savings is considered “electrification” and therefore subject to the electrification savings cap. | Courtney Golino | Splitting the algorithm/savings in to fuel switch and non-fuel switch sections was done in the heat pump measures but not in the clothes dryer (which happened to be the one in the volume 1 example). We have updated the clothes dryer calculation to also split them up and have applied it here too. Some additional language was also added to indicate that this should always be done for measures that have both fuel switch and non-fuel switch components. | Example updated and text added